Building Requirements

- Designer Qualifications- The designer must have the appropriate professional license in his/her area of expertise.

- Building Occupancy Classification- Occupancy classification is to be based upon an assessment of a projected chemical inventory of the building. Prior to the final design, the campus or designer will need to assign an occupancy class to insure compliance with the building codes.

Building Design Issues

- Special consideration should be given to the choice of fireproof construction for the buildings.

- It is prohibited to store, consume food, apply make-up or chew gum in areas where hazardous materials are used and/or stored.

- An automatically triggered main gas shutoff valve for the building shall be provided for use in a seismic event. In addition, interior manual shutoff valves shall be provided for both research and teaching areas.

- Large sections of glass shall be shatter resistant. In the event of a severe earthquake, as the glass in cabinets and windows breaks, the shards need to be restrained to prevent injury.

Laboratory Design Considerations

Walls/ Doors/Security

- The laboratory shall be completely separated from outside areas (i.e., must be bound by four walls). Having enclosed laboratories will help contain spills, keep unauthorized personnel from entering areas where hazardous operations are performed, etc. These regulations apply specifically to laboratories containing radioactive materials.

- The laboratory shall have means of securing specifically regulated materials such as DEA (Drug Enforcement Administration) controlled substances and CDC (Center for Diseases Control) select agents and radioactive materials (i.e., lockable doors, lockable cabinets, etc.). Having secured hazardous materials storage will keep unauthorized personnel from gaining access to them. These regulations apply specifically to laboratories containing radioactive materials

Windows

- If the laboratory has windows that open, they must be fitted with insect screens. Insects, particularly flies, are known to be a potential carrier of disease. To keep insects out of the lab, the doors must be closed while an experiment is in progress, and windows shall be screened if they are capable of being opened. These references apply specifically to laboratories containing biological materials

Flooring

- The floor must be non-pervious, one piece, and with covings to the wall. This can be achieved by use of glue, heat welded vinyl flooring, epoxy coated concrete slab, etc.

- Floors should be coved up walls and cabinets to ensure spills cannot penetrate underneath floors/cabinets. Tiles and wooden planks are not appropriate because liquids can seep through the small gaps between them. These references apply specifically to laboratories containing biological and radioactive

- Floors in storage areas for corrosive liquids shall be of liquid tight construction.

Sinks

- Each laboratory must contain a sink for hand washing.

- Exposure to hazardous materials and/or pathogenic organisms can occur by hand-to-mouth transmission. It is extremely important that hands are washed prior to leaving the laboratory. For this very reason, the sink should be located close to the egress. These references apply specifically to laboratories containing biological and radioactive materials.

- Laboratory sinks shall have lips that protect sink drains from spills.

- Sink lips or berms should be >= 0.25 inches and designed to completely separate the lab bench or fume hood work area from the sink drain.

Chemical/Waste Storage

- Chemical storage shelves shall not be placed above laboratory sinks.

- Sufficient space or facilities (e.g., storage cabinets with partitions) shall be provided so that incompatible chemicals/ gases (waste and non-waste) can be physically separated and stored. This will be based on the chemical inventory and use projection provided by the

- Materials, which in combination with other substances may cause a fire or explosion, or may liberate a flammable or poisonous gas, must be kept separate. When designing the shelves, it is important to factor in enough space for secondary containers. Recommend that solvent storage not be located under the laboratory fume hood, as this is a location where fires are most likely to occur in laboratories. All labs should be designed to conveniently and safely accommodate the temporary storage of biological, radiological, and chemicals (non-waste and waste) based on laboratory use projections. Wastes are generally stored in the lab in which they are generated, not in centralized accumulation areas.

Furniture Design, Location & Exit Paths

- All furniture must be sturdy. All work surfaces (e.g., bench tops and counters) must be impervious to the chemicals used. The counter top should incorporate a lip to help prevent run-off onto the floor.

- For example, many microbiological manipulations involve concurrent use of chemical solvents such as formaldehyde, phenol, and ethanol as well as corrosives. The lab bench must be resistant to the chemical actions of these substances and disinfectants. Wooden bench tops are not appropriate because an unfinished wood surface can absorb liquids.

- Also, wood burns rapidly in the event of a fire. Fiberglass is inappropriate since it can degrade when strong disinfectants are applied. Fiberglass also releases toxic smoke when burned. These references apply specifically to laboratories containing biological and radioactive materials.

- Vented cabinets with electrical receptacles and sound insulation should be provided for the placement of individual vacuum pumps, where their use is anticipated. A one- to two- inch hole for the vacuum line hose from the cabinet to the bench top should be provided.

- The lab shall have a minimum aisle clearance of at least 24 inches. Main aisles used for emergency egress must have a clearance width of at least 36 inches.

- Clear aisles and exits are necessary to facilitate departure in the event of an emergency. In practice, lab aisles must be designed wider than 24” so that even with the presence of lab stools and other miscellaneous items, a clearance of 24” is always maintained.

- A pathway clearance of 36 inches must be maintained at the face of the access/ exit door.

- Lab benches must not impede emergency access to an exit. This is also applicable to placement of other furniture and appliances such as chairs, stools, refrigerators, etc.

- Designated storage space should be provided for lab carts. Location must not reduce width of corridors or aisles to less than code-required widths. Lab carts should be secured with earthquake restraints when not in use.

- Furniture design must comply with basic ergonomic specifications

- Lack of properly designed workstations can increase safety and ergonomic risks for occupants.

- Laboratory shelving should NOT be installed at heights and distances which require workers to reach 30 centimeters above shoulder height and extend arms greater than 30 centimeters while holding objects 16 kg or less when standing on the floor or on a 12” step stool.

- Installation of high shelving, above laboratory benches in particular, can create several potential hazards, including, but not limited to ergonomic issues (over reaching above shoulders and across lab benches); spill and exposures to chemicals, radiological or biological agents (e.g., dropping containers when accessing them at high levels). If high shelving were installed, administrative controls, which are often burdensome, would be required. A system for ensuring safe access would include prohibition on the materials stored on shelves, limitations on the frequency of use, availability of ladders or ladders stands, training on ladders, etc

- The space between adjacent workstations and laboratory benches should be 5 ft or greater to provide ease of access. In a teaching laboratory, the desired spacing is 6 ft. Bench spacing shall be considered and included in specifications and plans.

- The laboratory doors shall be automatically self-closing. Such self-closing doors are to be able to be opened with a minimum of effort as to allow access and egress for physically challenged individuals.

- Doors in H-occupancy laboratories shall have doors which swing in the direction of egress. Doors serving B-occupancy shall swing in the direction of egress if the occupant load is 50 or more. Where possible, all B-occupancy lab doors should swing out.

- Doors, which swing in the direction of egress, will facilitate occupant departures from laboratories during emergencies.

- Lab desks should be located near exit ways and in the path of fresh make up air.

- Will ensure that in the event of an emergency, employees working in “clean” areas (i.e., their desk) do not have to pass through more hazardous areas to exit the laboratory.

Illumination

- Laboratory areas shall be provided adequate natural or artificial illumination to ensure sufficient visibility for operational safety.

Earthquake Restraints

- All equipment requiring anchoring shall be anchored, supported and braced to the building structure. For example, any equipment, including but not limited to, appliances and shelving that are 60 inches or higher and have the potential for falling over during an earthquake, shall be permanently braced or anchored to the wall and/or floor.

- This practice keeps these items from falling in the event of an earthquake and assures safety while exiting is not compromised.

- All shelves must have a passive restraining system such as seismic shelf lips (3/4 inch or greater). The shelves themselves must be firmly fixed so they cannot be vibrated out of place and allow shelf contents to fall.

- Installation of seismic lips on shelving areas will prevent stored items from falling during a seismic event.

- All equipment requiring anchoring, whether installed by a contractor or the

- University, shall be anchored, supported, and braced to the building structure

- Cabinets must be equipped with positive locking door latches.

Clean ability

- The laboratory shall be designed so that it can be easily cleaned. Bench tops must be a seamless one-piece design to prevent contamination. Laminate bench tops are not suitable. Penetrations for electrical, plumbing, and other considerations must be completely and permanently sealed. If the bench abuts a wall, it must be coved or have a backsplash against the wall. Walls should be painted with washable, hard non-porous paints.

- Spaces between benches, cabinets, and equipment must be accessible for cleaning and allow for servicing of equipment.

- Laboratory furniture must have smooth, non-porous surfaces so as to resist the absorption of liquids and the harsh effects of disinfectants. Furniture must not be positioned in such a manner that makes it difficult to clean spilled liquids or conduct routine maintenance.

Break rooms

- The design of the laboratory building must incorporate adequate additional facilities for food storage/consumption and personal hygiene tasks.

- The storage and consumption of food, application of cosmetics or lip balm, or handling of contact lens in areas they may be contaminated by any toxic material or blood borne pathogen is prohibited.

F. Mechanical Considerations

Electrical

- Shall provide GFI protection to electrical receptacles above counter tops and within 5 feet of sinks. Receptacles that are not readily accessible or receptacles for appliances occupying dedicated space, which are cord-and-plug connected.

- The lab should be fitted with an adequate number of electrical outlets, which can accommodate electrical current requirements with an additional 20-40% capacity.

- The lab may have several pieces of equipment, which require large amounts of electrical current. Such items include freezers, biosafety cabinets, centrifuges, and incubators. The room design must take into consideration concerns such as electrical demand prior to occupancy to avoid a potential power failure.

- Circuit breakers should be located outside the lab, but not in rated corridors.

- In the event of an emergency, the laboratory may be unsafe to enter. Hence, the circuit breakers for key electrical appliances should be located outside the lab.

Plumbing

- Auxiliary valves for gas and vacuum lines should be located outside the lab.

- In the event of an emergency, the laboratory may be unsafe to enter. Hence, the valves for gas and vacuum lines should be located outside the lab.

- Flexible connections should be used for connecting gas and other plumbed utilities to any freestanding device, including but not limited to biosafety cabinets, incubators, and liquid nitrogen freezers. Flexible connections should be appropriate for the pressure requirements and should be constructed of material compatible with the transport gas. A shutoff valve should be located within sight of the connection and clearly marked.

- Seismic activity may cause gas and other utility connections to break off. A flexible connection will minimize this potential considerably.

- Sink drains traps shall be transparent (e.g., made of glass) and or easy to inspect or have drain plugs to facilitate mercury spill control, if mercury-containing products or compounds will not be used.

More on Chemical Storage

- The storeroom floor shall be unobstructed and shall not be used as a storage area.

- The storeroom floor shall be equipped with a drainage system of sufficient capacity to provide fast and thorough flushing of spilled reagents. The drainage system shall direct the flow of hazardous materials to an approved location, or the room, building, or area shall be designed to provide secondary containment for the hazardous materials. Secondary containment shall be designed to contain a spill from the largest single container or tank plus the flow rate of the automatic fire-extinguishing system, for a flow period of twenty (20) minutes, for the area of the room or area in which the storage is located or the system design area, whichever is smaller.

- The chemical storage cabinets or storage room shall be kept under lock and key and controlled by the person in charge.

- Only those areas of the storage room specifically designed for chemical storage and meeting other requirements of this section shall be used for chemical storage. Heavy bottles and large bottles of acids shall be stored near the floor and protected from breakage.

- Chemicals shall not be stored above the eye level of the person handling the chemicals.

- Chemicals, which react with each other, shall not be stored in close proximity to each other.

- Adequate shelving shall be provided to prevent the chemicals from becoming overcrowded and inaccessible.

- An inventory, which is updated periodically, of all chemicals shall be maintained and be readily available.

- Only small amounts of hazardous, explosive, or dangerous chemicals shall be kept on hand.

- Laboratory storage rooms shall have manual or mechanical ventilation.

- Chemical storage shall be on shelving with protective safety lips.

- Chemicals shall be stored in chemically compatible families.

- Store only the minimum quantity of flammable chemicals needed.

- Store flammables in approved flammable storage cabinets.

- The floors of chemical storage rooms shall not be carpeted. The floor covering of a chemical room shall be of a material that will not react with stored chemicals.

- Laboratory fume hoods shall not be used for the storage of chemicals.

- Flammable liquids shall not be stored in refrigerators unless the refrigerator is designed and approved for flammable storage.

- Chemicals shall not be stored near, over, or under a sink.

- Flammables and oxidizers shall not be stored near each other.

- Nitric acid shall not be stored with other acids unless the storage cabinet is provided with a separate compartment specifically for nitric acid.

- Laboratories and chemical storerooms shall have a spill control center equipped with commercial spill control products, fine clay, kitty litter, or vermiculite. Additionally laboratories and chemical storerooms shall have materials for neutralization of chemicals in their spill control center.

- Every chemical storage area shall be equipped with emergency eye wash stations capable of meeting the flushing requirements of the most hazardous chemical that could be encountered in the storage area.

- Every chemical storeroom shall be equipped with an emergency overhead shower.

Summary

Segregation of chemicals by class within appropriate cabinets is the key idea. One may not merely arrange substances on a shelf alphabetically without regard to their chemical characteristics. Solvents must have their own special fire-resistant cabinets; oxidants are stored away from reductants; acids are stored away from bases; and peroxidizables are monitored and discarded at regular intervals. A good idea is color-coding the edges of the shelves to match the color coding for the category of substance stored there. Within, each category, materials can be arranged alphabetically. More details on the color-coding scheme are available:

It is strongly recommended that chemical storage within research and teaching laboratories be minimized. Again, buy the minimum practical quantity; use it promptly after purchase, and dispose of any excess.

Rooms chosen for chemical storage should be well ventilated and preferably equipped with an exhaust fan that will accomplish at least six air changes per hour.

Significant quantities of chemicals should not be stored in a room that is regularly occupied by students or faculty who are not conducting experiments. Furthermore, consumption or storage of food or beverages of ANY kind is strictly forbidden in rooms where chemicals are stored or used!

The most cost effective shelving is steel with acid-resistant paint; next best is wood with acid-resistant paint. Shelving should be labeled clearly to indicate what kinds of chemicals might be stored there. As noted above, an easy way to do this is to color-code the edges of shelves with paint or tape to match the color-coding of labels; materials then can be returned to proper storage at a glance.

Storage areas must be equipped with fire extinguishers, eyewash fountains, and materials for cleaning up spills. Kitty litter is excellent for this latter purpose, being both adsorbent and inert. A five-gallon bucket of litter will absorb the contents of a standard 2 L reagent bottle. Surround the spill with litter to contain it, and then cover it completely. Sweep it up with implements kept specifically for that purpose. Contaminated litter then is placed into a heavy plastic bag, and arrangements made for its pickup by EH&S, as described below.

Fume hoods normally should not be used for storage of chemicals. When such storage cannot be avoided, because properly ventilated cabinets are not available, or because the compounds are particularly odiferous (e.g., thiols), the bottles must be placed in a plastic tub or tray to contain any leakage or spill. Hoods being used for storage may not be used for experimentation, and should be labeled clearly as storage hoods.

PROGRAM MANU